# H2S Dry Scrubber – Odor Control

## Technical Description of the Product

- The absorbent combines premium quality activated carbon together with a blend of catalytically active inorganic phases

- Mechanism: H2S is catalytically oxidized to sulfur (S) in the active sites on metal oxides. Next, sulfur migrates and builds up in the micropores of the activated carbon phase. Thus, the metal oxides are available again to oxidize new H2S molecules

- H2S is not converted to sulfuric acid which may lead to equipment corrosion problems

## Added Benefits

- High H2S removal efficiency (> 99%) upon variable inlet conditions

- Sulfur loading is not affected in the presence of high CO2 levels

- Does not require frequent change outs or time consuming regenerating processes

- Safe to handle and use

- The high ignition temperature (420 ºC) minimizes the risk of bed fire

- Low pressure drop, due to the nominal pellet diameter (4 mm)

- Does not need to undergo long term conditioning prior to being put into operation

## Applications

Any use that requires control of H2S gas, such as:

- Wastewater treatment plants

- Pumping stations

- Wet wells

- Lift stations

- Sludge holding tanks

- Refineries

- Pulp and paper mills

- Composting

Benchmark

See following chart to appraise how the absorbent compares to counterpart products from other manufacturers across the globe

|  | Purafil Odorcarb Ultra |
| --- | --- |
|  | US Filter Midas OCM |
|  | Jacobi Addsorb Sulfox |
|  | New Product |

Testing

The absorbent has been tested several times (>100) against H2S absorption capacity, following the directions of ASTM 6646-03, which account for:

- Contact time: 4,8 seconds

- Inlet H2S Concentration: 10.000 ppmv (= 1% v/v)

- 80% relative humidity inlet gas

- Balance gas: pre-filtered air from the environment

- Breakthrough measured at outlet H2S concentration of 50 ppm (= 99.5% efficiency)

Also, a TGA analysis proves that elemental sulfur is formed.

|  | Fresh product |
| --- | --- |
|  | Spent product |

Specifications

| SPECIFICATIONS |  |
| --- | --- |
| H2S removal capacity | 0.8 g H2S/ g media, min. |
| Nominal pellet diameter | 4 mm (other diameters possible) |
| Moisture content | 25% max. |
| Bulk density | 460 ± 20 g/cm3 |
| Loss on attrition | 4.5% max. |
| Ignition temperature | 420 ºC (UL2) |
| pH of spent carbon | Neutral |

Field Study

This product has been successfully tested in several countries and applications.

Among them, one of the largest WWTP of Spain (255.000 m3/day). The product was tested after experiencing fire hazards and low bed life with traditional alkali impregnated activated carbon.